Inspection form summary

| Section | Name | Actions required |
| --- | --- | --- |
| 1.0 | Registration and notification | Confirm registration particulars |
| 2.0 | System plans | Assess plans for compliance |
| 3.0 | Operating and maintenance manuals | Assess manuals for compliance |
| 4.0 | Responding to detection of Legionella in water samples | Obtain copies of all notifiable results (18 months) and assess log books for compliance. |
| 5.0 | Maintenance log books | Assess log books for compliance and determine compliance with maintenance requirements |
| 6.0 | Physical aspects | Detail system information |
| 7.0 | Storage of heated water | Determine compliance with requirement relating to storage of heated water |
| 8.0 | Systems serving susceptible populations | Detail susceptibility of exposed population and presence of risk management strategies. |
| 9.0 | Microbiological testing | Collect water samples for Legionella testing |
| 10.0 | Systems to be operated and maintained by competent persons | Assess competence of responsible person |
| 11.0 | Independent inspector declaration | Completed and signed by independent inspector |
| 12.0 | Assessment details and acknowledgement | Completed and signed by system owner or responsible person, inspector and assessing authorised officer |
|  | Compliance summary | One page summary of regulatory compliance findings. |

|  | Inspection and assessment of plans, manuals, procedures and records. |
| --- | --- |
|  | Inspection and assessment of physical system infrastructure. |

Colour coding instructions

|  | Do not alter grey shaded sections of the form |
| --- | --- |
|  | Independent inspectors or local council authorised officers: complete all unshaded sections of the form prior to providing system owner with a copy of the completed report. |
|  | Independent inspectors or local council authorised officers: indicate compliance (✓), non-compliance (✗) or not applicable (N/A) |
|  | These sections should not be completed by an independent inspector. Local council authorised officers should complete these sections only. |

Suggested guidelines for setting and adjusting inspection frequency

Regulation 15 of the South Australian Public Health (Legionella) Regulations 2013 requires the local authority to ‘at least once in every 12 months’ cause an inspection of each high risk manufactured water system registered with the authority to be carried out’ by an authorised officer of the authority or a competent independent inspector.

When extensive or serious non compliance is identified as a result of a routine inspection, routine inspection frequency (in addition to follow-up inspections) should be increased until the system is found to be fully compliant as a result of a further routine inspection.

Inspection frequency according to risk factors for Legionella susceptibility:

| Likelihood of individuals potentially exposed to aerosol generated by the system having risk factors for Legionella susceptibility | Inspection frequency (months) |
| --- | --- |
|  | Starting point | Maximum | Minimum |
| Very high (likely that susceptible individuals could be exposed). | 12 | 3 | 12 |
| Moderate (unlikely that any susceptible individuals could be exposed) | 12 | 6 | 12 |
| Low (very unlikely that any susceptible individuals could be exposed) | 12 | 12 | 12 |

Due to the prevalence of individuals with risk factors for Legionella susceptibility (see below) in the general population in Australia, nearly all cooling water systems located in workplaces and populated areas and warm water systems serving workplaces, hospitals, care facilities and public buildings would have a very high likelihood of exposing susceptible individuals to aerosol generated.

Risk factors for an individual’s Legionella susceptibility:

|  | Community acquired | Travel associated | Nosocomial (hospital acquired) |
| --- | --- | --- | --- |
| Risk factors (personal/individual) | Age >40 years; male; underlying disease such as diabetes; chronic heart disease; smoking; immunosuppression (especially with glucocorticosteroids and chronic debilitating illness); structural pulmonary comorbidity; chronic renal failure; recent travel; haematological malignancy; iron overload; other immunosuppression | Age >40 years; male; heavy smoking, alcohol abuse; change in lifestyle; underlying disease such as diabetes; chronic heart disease, other immunosuppression | Age >25 years; transplant patient; other immunosuppression; surgery, especially head and neck; cancer, including leukaemias/ lymphomas; diabetes; treatment with respiratory devices; chronic heart/lung disease; smoking, alcohol abuse |

Adjustment of inspection frequency:

| Inspection frequency adjustment | Number and type of non compliance |
| --- | --- |
| Increase if | Five or more non-compliances (not serious), or One or more serious non-compliances |
| Decrease if | No non compliances |

| Registered system details (to be completed from authority’s register prior to inspection) | (✓) – details correct | © SA Health Government of South Australia. All rights reserved. |
| --- | --- | --- |
| Premises Name |  |  | Ref No |  |
| Premises address |  |  | Date |  |
| Owner of premises - full name |  |  | Time |  |
| Business address |  |  | Officer |  |
| Residential address |  |  | Inspection Type |
| Responsible person - full name |  |  | Scheduled |  |
| Business address |  |  | Random |  |
| Business telephone |  |  | Complaint |  |
| Residential address |  |  | Investigation |  |
| Residential telephone |  |  | Other |  |

All relevant sections of this form must be completed in full as per the directions provided throughout.

| Enter any changes to the system registration details which have not yet been notified to the relevant authority | Date details changed |
| --- | --- |

Indicate compliance (✓), non-compliance (✗) or not applicable (N/A).    (SNC) indicates a serious non compliance.

Competent Independent Inspectors should notify the local authority of all serious non compliance within 24 hours.

| 1.0 Registration and notification |
| --- |
| # | Description | Reg. | Compliance | Comments |
| 1.1 | Is the system registered? (within 1 month of being brought into service) (SNC) | 5(2) |  |  |
| 1.2 | Have any particulars changed with regards to registration of the system? (changed over 1 month ago without notification?) | 6(4) |  |  |
| 1.3 | Has the system been permanently decommissioned or removed? (over 1 month ago without notification?) | 6(5) |  |  |

2.0 System plans

From October 2009, compliant plans of warm water systems must be kept on the premises in a readily accessible place.

A copy of the system plans must be attached to this report.

| 2.1 | On what date was the system installed? |  |
| --- | --- | --- |
| 2.2 | On what date was the system commissioned? |  |
| 2.3 | Are plans of the system made readily available for inspection (and kept in a readily accessible place)? | Yes / No |

ANSWER THE FOLLOWING QUESTION FOR SYSTEMS INSTALLED BEFORE 1 OCTOBER 2009

| 2.4 | Do the plans show the location of all major components of the system, including: cooling towers, condensers, filtration devices, automatic biocide dosing devices, drift eliminators, water inlets, waste outlets and discharge points, water heating devices and water storage facilities? | Yes / No |
| --- | --- | --- |

ANSWER THE FOLLOWING QUESTION FOR SYSTEMS INSTALLED ON OR AFTER 1 OCTOBER 2009

| 2.5 | Do the plans show the location of all parts of the system, including and in addition to: cooling towers, condensers, filtration devices, automatic biocide dosing devices, drift eliminators, water inlets, waste outlets and discharge points, water heating devices and water storage facilities? | Yes / No |
| --- | --- | --- |
| Comments |

| # | Description | Reg. | Compliance | Comments |
| --- | --- | --- | --- | --- |
| 2.6 | Are compliant plans for the system kept on the premises in a readily accessible place and made available for inspection on request by an authorised officer? | 10(1) |  |  |
| Comments, non-compliance details and action to be taken with due dates. (This section should only be completed by an authorised officer) |

Please complete all actions listed above by the specified due dates

3.0 Operating and maintenance manuals

Compliant operating and maintenance manuals for warm water systems must be kept on the premises in a readily accessible place.

| 3.1 | Are operating and maintenance manuals for the system made readily available for inspection (and kept in a readily accessible place)? | Yes / No |
| --- | --- | --- |

IS THE FOLLOWING INFORMATION INCLUDED IN THE OPERATING AND MAINTENANCE MANUALS?

| 3.2 | Physical details of the plant, equipment and systems and pre-treatment carried out. | Yes / No |
| --- | --- | --- |
| 3.3 | Procedures for maintenance including water treatment management and monthly physical inspections. (refer 5.9) | Yes / No |
| 3.4 | Cleaning, disinfection and decontamination procedures. Decontamination procedures must be as per the procedure set out in Schedule 3 Part 1 of the Guidelines for the Control of Legionella in Manufactured Water Systems in South Australia or by a procedure approved by the Minister. (refer 5.12) | Yes / No |

** Where applicable, a copy of the Minister’s approval must be attached to this report **

| 3.5 | Legionella sampling procedures as per Schedule 2 of the Guidelines for the Control of Legionella in Manufactured Water Systems in South Australia. | Yes / No |
| --- | --- | --- |
| 3.6 | Legionella detection response procedures as per Schedule 4 Part 2 of the Guidelines for the Control of Legionella in Manufactured Water Systems in South Australia. | Yes / No |
| 3.7 | Start-up, operating and shut-down procedures. | Yes / No |
| 3.8 | Schedules for the maintenance management program, including: plant servicing, water treatment, monthly physical inspection and temperature testing, decontamination and cleaning schedules. (refer 5.7 & 5.9) | Yes / No |
| Comments |

| # | Description | Reg. | Compliance | Comments |
| --- | --- | --- | --- | --- |
| 3.9 | Are compliant operating and maintenance manuals for the system kept on the premises in a readily accessible place and made available for inspection on request by an authorised officer? | 10(3) |  |  |
| Comments, non-compliance details and action to be taken with due dates. (This section should only be completed by an authorised officer) |

Please complete all actions listed above by the specified due dates

4.0 Responses to detection of Legionella in water samples

Attach copies of all lab reports for water samples taken from this system where the results indicated the presence of 10 or more colony forming units of Legionella per mL of water for samples collected during the last 18 months.

| Number of notifiable Legionella results attached | Frequency of Legionella sampling/testing | Sample collection points | Do the records indicate that the system was immediately shut down or decontaminated upon receipt of all attached results? | Do the records indicate that the local authority was notified of all attached results within 24 hours of the receipt of the reports? |
| --- | --- | --- | --- | --- |
|  |  |  | Yes / No | Yes / No |

Comments

| (This section should only be completed by an authorised officer) Authority records should be checked to confirm that the listed notifications were received |
| --- |
| # | Description | Reg. | Compliance | Comments |
| 4.1 | Has the authority been notified within 24 hours of the results of all microbiological testing of water taken from the system indicating the presence of 10 or more cfu of Legionella per mL of water? (SNC) | 17(1) |  |  |
| 4.2 | Was the system immediately shut down or decontaminated upon receipt of any result indicating the presence of 10 or more cfu of Legionella per mL of water? (SNC) | 17(1) |  |  |
| Comments, non-compliance details and action to be taken with due dates. (This section should only be completed by an authorised officer) |

Please complete all actions listed above by the specified due dates

5.0 Maintenance log books

Up to date, compliant, maintenance log books for warm water systems and associated plant and equipment must be kept on the premises in a readily accessible place.

| 5.1 | Are maintenance log books for the system made readily available for inspection (and kept in a readily accessible place)? | Yes / No |
| --- | --- | --- |

IS THE FOLLOWING INFORMATION RECORDED IN THE MAINTENANCE LOG BOOKS?

| 5.2 | For all cleaning, servicing and other work: date, item of plant, equipment or system and nature of service or cleaning performed. | Yes / No |
| --- | --- | --- |
| 5.3 | Details of defects found and rectification procedures undertaken. | Yes / No |
| 5.4 | The name of the person AND company performing the work. | Yes / No |
| 5.5 | Details of all microbiological test results (including non-detection) of samples of water taken from the system. | Yes / No |
| 5.6 | Details of all responses to Legionella detection in the system and the outcome of such responses. | Yes / No |
| 5.7 | Evidence that the temperature of water in storage areas and throughout the distribution of the system measured at least once every month and recorded in the maintenance log book (refer 3.8). | Yes / No |
| 5.8 | Evidence that water in storage areas of the system kept at a temperature of at least 60°C at all times while the system is in operation. | Yes / No |
| 5.9 | Evidence that a physical inspection of the system is carried out at least once every month to examine the cleanliness and mechanical condition of the system (refer 3.3, 3.8 & 5.11). | Yes / No |
| 5.10 | Evidence that the system is thoroughly cleaned whenever an inspection reveals sludge, slime, scale, foam, rust, dirt or other impurities or foreign material present in the system. | Yes / No |
| 5.11 | Details and results of all monthly physical inspections (refer 5.9). | Yes / No |
| 5.12 | Evidence that decontamination of the system is carried out at least every 6 months in accordance with a prescribed or approved decontamination procedure (refer 3.4 & 5.13) | Yes / No |
| 5.13 | Details of all decontaminations performed including all outlet testing results and testing equipment used (refer 5.12). | Yes / No |
| Comments |

| # | Description | Reg. | Compliance | Comments |
| --- | --- | --- | --- | --- |
| 5.14 | Are compliant maintenance log books for the system kept on the premises in a readily accessible place and made available for inspection on request by an authorised officer? | 14(1) |  |  |
| 5.15 | Have all maintenance log books been retained for a period of at least five years after the last entry in the log book is made (since October 2008)? | 14(2) |  |  |
| 5.16 | Is the system maintained in complete compliance according with the mandatory requirements of the regulations? (SNC) | 13 |  |  |
| Comments, non-compliance details and action to be taken with due dates. (This section should only be completed by an authorised officer) |

Please complete all actions listed above by the specified due dates

6.0 Physical aspects of warm water system

SAA/SNZ HB32:1995 provides guidance to inspectors for the physical parameters to be considered in order to effectively control microbial growth in warm water systems. Complete the following physical inspection checklist for all towers in the system. If the relevant authority determines that the condition of the system represents potential risk to public health or a breach of the general duty, the local authority may issue a notice under section 92 of the South Australian Public Health Act 2011, requiring the owner to take certain specified action. A person to whom a notice is issued must not, without reasonable excuse, fail to comply with the notice. Maximum penalty $25000.

| Parameter |  | Comments |
| --- | --- | --- |
| Are all hot water storage cylinders, calorifiers, expansion, feed and water storage tanks clearly labelled? | Yes / No |  |
| Are all mixing valves (including TMVs) accessible for service and maintenance? | Yes / No |  |
| Are all thermostatic mixing valves manufactured in compliance with AS4032.1? | Yes / No |  |
| Is the warm water pipe work from thermostatic mixing valves to each associated outlet no less than 1m and no more than 6m long? | Yes / No |  |
| Are all mixing valves associated with bathing facilities serviced, maintained and internally cleaned in accordance with the manufacturers’ instructions and AS4032.3 (at least once every 12 months)? (including cleaning of any associated line strainers and inbuilt strainers) | Yes / No |  |
| Concurrently with commissioning and servicing of mixing valves, is the temperature controlling device or thermostat removed from the valve and then the mixing valve and all associated taps and outlets decontaminated as per Part 2 of Schedule 3 of the Guidelines for the Control of Legionella in manufactured Water Systems in South Australia? (the temperature control mechanism should be washed separately and also decontaminated) | Yes / No |  |
| If pasteurisation is used as a method of disinfection, does the documented procedure include steps to prevent scalding of end users during the process, and provision of adequate ventilation to aid in the removal of heated water vapour? | Yes / No |  |
| Following pasteurisation, is the complete warm water system flushed thoroughly with cold water so as to remove any hot, scalding water? | Yes / No |  |
| Comments |

PROVIDE INFORMATION ON THE SYSTEM WATER HEATERS AND HOT WATER STORAGE BELOW:

|  | Type | Make, Model & serial no | Storage temperature (measured) | Description and storage capacity | Location |
| --- | --- | --- | --- | --- | --- |
| Heater 1 |  |  |  |  |  |
| Heater 2 |  |  |  |  |  |
| Heater 3 |  |  |  |  |  |
| Heater 4 |  |  |  |  |  |
| Heater 5 |  |  |  |  |  |
| Heater 6 |  |  |  |  |  |
| Storage 1 |  |  |  |  |  |
| Storage 2 |  |  |  |  |  |
| Storage 3 |  |  |  |  |  |
| Storage 4 |  |  |  |  |  |
| Storage 5 |  |  |  |  |  |
| Storage 6 |  |  |  |  |  |
| Comments |

PROVIDE INFORMATION ON THE NUMBER OF WARM WATER OUTLETS IN THIS SYSTEM:

|  | Bath | Shower | Hand basin | Other |
| --- | --- | --- | --- | --- |
| Number of outlets |  |  |  |  |
| Comments |

PROVIDE INFORMATION ON THE NUMBER OF MIXING VALVES IN THIS SYSTEM

|  | TMVs | Tempering valves | Other (provide details) |
| --- | --- | --- | --- |
| Number of valves |  |  |  |
| Comments |

7.0 Storage of heated water

AT THE TIME OF INSPECTION:

| 7.1 | Is water in storage areas of the system at a temperature of at least 60°C? | Yes / No |
| --- | --- | --- |
| Comments |
| # | Description | Reg. | Compliance | Comments |
| 7.2 | Is the temperature of stored heated water in the system maintained in complete compliance according to the regulations? (SNC) | 13 |  |  |
| Comments, non-compliance details and action to be taken with due dates. (This section should only be completed by an authorised officer) |

Please complete all actions listed above by the specified due dates

8.0 Systems serving susceptible populations

Elderly and immune compromised people are particularly susceptible to Legionella infection. The following requirements should be observed with regards to warm water systems in facilities serving susceptible populations, including, nursing homes, hospitals, aged care facilities and supported residential facilities. The local authority may issue a notice under section 92 of the South Australian Public Health Act 2011 in order to require compliance with these requirements.

BASED ON THE PHYSICAL INSPECTION, OPERATING AND MAINTENANCE MANUALS, MAINTENANCE LOG BOOKS AND INFORMATION PROVIDED BY THE RESPONSIBLE PERSON,

| 8.1 | Does the system serve susceptible people? | Yes / No |
| --- | --- | --- |
| 8.2 | At least once a week, are all warm water outlets not used in the previous seven days flushed until the correct operating temperature is reached at the outlet? | Yes / No |
| 8.3 | Are any dead legs evident in the system? | Yes / No |
| 8.3 | Has an effort been made to identify and eliminate dead legs in the system? | Yes / No |
| Comments |

| # | Description | Reg. | Compliance | Comments |
| --- | --- | --- | --- | --- |
| 8.4 | Is the system operated in accordance with the recommended practices for facilities serving susceptible populations? | n/a |  |  |
| Comments, non-compliance details and action to be taken with due dates. (This section should only be completed by an authorised officer) |

Please complete all actions listed above by the specified due dates

9.0 Microbiological testing

As part of the system compliance assessment, at least two water samples must be collected and tested for Legionella including one sample from the outlet most distal from the heat source. If the system contains more than 66 outlets, a number of samples should be collected for testing equivalent to 1 representative sample per each 33 outlets in the system rounded up to the next full number.

- Where possible, samples should be collected from outlets where the plans, pipe work, records and temperature profile indicate that stagnation may be occurring.

- Samples must be collected and transported as per Schedule 2 of the Guidelines for the Control of Legionella in Manufactured Water Systems in South Australia.

- Samples must be tested by a NATA accredited laboratory in accordance with AS/NZS 3896.

- Samples must be processed within 24 hours of collection.

- A copy of all sample result reports must be provided to the responsible person so that results can be recorded in the maintenance log books.

MANDATORY TESTING SAMPLES SHOULD NOT BE COLLECTED WITHIN 14 DAYS FOLLOWING A SYSTEM DECONTAMINATION EVENT

| Date of last system decontamination | Decontamination method (chlorination/pasteurisation/other) | Reason for last system decontamination | Date of next scheduled system decontamination |
| --- | --- | --- | --- |

** A copy of the sample test results must be attached to this report **

RECORD THE INFORMATION ON ALL SAMPLES COLLECTED BELOW:

| Unique sample identification number | Detailed description of sampling point. | Date collected | Time collected | Results: Legionella cfu/mL and type |
| --- | --- | --- | --- | --- |
| Comments and follow-up upon receipt of sample results |

10.0 Systems to be operated and maintained by competent persons

BASED ON THE PHYSICAL INSPECTION, OPERATING AND MAINTENANCE MANUALS, MAINTENANCE LOG BOOKS AND INFORMATION PROVIDED BY THE RESPONSIBLE PERSON, IS THE RESPONSIBLE PERSON:

| 10.1 | Knowledgeable in the operation and maintenance of the system? | Yes / No |
| --- | --- | --- |
| 10.2 | Sufficiently competent to ensure that the system is operated and maintained as required by the regulations? | Yes / No |
| Comments |

| # | Description | Reg. | Compliance | Comments |
| --- | --- | --- | --- | --- |
| 10.3 | Is the person nominated by the owner as the person responsible for the operation and maintenance of the system competent as defined by the regulations? | 11 |  |  |
| Comments, non-compliance details and action to be taken with due dates. (This section should only be completed by an authorised officer) |

Please complete all actions listed above by the specified due dates

11.0 Independent Inspector declaration

If this inspection has been conducted in order to satisfy the requirements of a notice issued by the local authority pursuant to Reg 15(2), the Independent Inspector must complete the following declaration:

| 11.1 | I am a genuine independent third party with respect to this system. Neither I nor any company or individual with which I am professionally or personally associated has any involvement in the operation, treatment, maintenance or cleaning of this system. I am not the owner of the system, nor am I an employee, relative or personal friend of the owner of the system. I am satisfied that there is no real or perceived conflict of interest which would prevent me from making or being perceived to make an open, honest and comprehensive compliance assessment of this system. | Yes / No |
| --- | --- | --- |
| 11.2 | I am knowledgeable in the operation and maintenance of this warm water system | Yes / No |
| 11.3 | Provide an overview of your knowledge of the operation and maintenance of this warm water system. |  |
| 11.4 | I have a comprehensive understanding of the South Australian Public Health (Legionella) Regulations 2013 (the Legionella Regulations), such as to enable me to assess this system in order to determine whether it is operated and maintained in compliance with all relevant requirements of the Legionella Regulations. | Yes / No |
| 11.5 | I have qualifications or training in water treatment of warm water systems. | Yes / No |
| 11.6 | Provide details of your qualifications or training in water treatment of warm water systems. *A copy of any evidence of your qualifications and/or training must be attached to this report * |  |
| 11.7 | In the process of conducting the compliance inspection and assessment of this system, the owner or responsible person has provided complete access to all parts of the system and related records and has provided all necessary information to enable a complete and thorough compliance assessment to be conducted. | Yes / No |
| 11.8 | If you answered No above (at 11.7), please provide details of the necessary access or information which was not made available to you, and how that impacted on your ability or capacity to assess the system for compliance. |  |

12.0 Assessment details and acknowledgement

Upon completion of the site inspection, the following section must be completed and signed by the inspector and by the system owner or responsible person.

Please indicate the time spent conducting this assessment.

| Travelling time | Time spent on site | Delivery of water samples to lab | Paperwork, report, & correspondence |
| --- | --- | --- | --- |

| I have read and understand the contents of this assessment. Name of system owner or responsible person: | Inspector’s name | Inspector’s contact phone numbers |
| --- | --- | --- |
| Signature of system owner or responsible person: Date: | Inspector’s signature: Date: |
| Environmental Health Officer assessing report on behalf of the authority. (This section should only be completed by an authorised officer) |
| Further action? | Nil |  | Re-inspection |  | Letter |  | Issue notice |  | Expiation |  | Prosecution |  |
| I have read and understand the contents of this assessment and have taken appropriate action to rectify any non-compliance noted in the report. Where necessary, I have requested further information. Name and signature of assessing environmental health officer: | Date this report was received by the authority. | Date of EHO assessment. |
| Routine inspection frequency: | Previous | New |

- When completed in full, a copy of this report must be mailed to the system owner by the authority.

COMPLIANCE SUMMARY

| System and contact details | © SA Health, Government of South Australia. All rights reserved. |
| --- | --- |
| Premises Name |  | Ref No |  |
| Premises address |  | Date |  |
| System name/description |  | Time |  |
| Business telephone |  | Officer |  |
| # | Description | Maximum Penalty | Expiation | Reg # | Compliance? |
| 1.0 Registration and notification |
|  | Is the system registered? (within 1 month of being brought into service) (SERIOUS NON COMPLIANCE) | $5000 | $315 | 5(2) |  |
|  | Have any particulars changed with regards to registration of the system? (changed over 1 month ago without notification?) | $750 | $80 | 6(4) |  |
|  | Has the system been permanently decommissioned or removed? (over 1 month ago without notification?) | $750 | $80 | 6(5) |  |
| 2.0 System plans |
|  | Are compliant plans for the system kept on the premises in a readily accessible place and made available for inspection on request by an authorised officer? | $1250 | $160 | 10(1) |  |
| 3.0 Operating and maintenance manuals |
|  | Are compliant operating and maintenance manuals for the system kept on the premises in a readily accessible place and made available for inspection on request by an authorised officer? | $1250 | $160 | 10(3) |  |
| 4.0 Responses to detection of Legionella in water samples |
|  | Has the authority been notified within 24 hours of the results of all microbiological testing of water taken from the system indicating the presence of 10 or more cfu of Legionella per mL of water? (SERIOUS NON COMPLIANCE) | $5000 | $315 | 17(1) |  |
|  | Was the system immediately shut down or decontaminated upon receipt of any result indicating the presence of 10 or more cfu of Legionella per mL of water? (SERIOUS NON COMPLIANCE) | $5000 | $315 | 17(1) |  |
| 5.0 Maintenance log books |
|  | Are compliant maintenance log books for the system kept on the premises in a readily accessible place and made available for inspection on request by an authorised officer? | $1250 | $160 | 14(1) |  |
|  | Have all maintenance log books been retained for a period of at least five years after the last entry in the log book is made (since October 2008)? | $1250 | $160 | 14(2) |  |
|  | Is the system maintained in complete compliance according with the mandatory requirements of the regulations? (SERIOUS NON COMPLIANCE) | $5000 | $315 | 13 |  |
| 7.0 Storage of heated water |
|  | Is the temperature of stored heated water in the system maintained in complete compliance according to the regulations? (SERIOUS NON COMPLIANCE) | $5000 | $315 | 13 |  |
| 8.0 Systems serving susceptible populations |
|  | Is the system operated in accordance with the recommended practices for facilities serving susceptible populations | n/a | n/a | n/a |  |
| 10.0 Systems to be operated and maintained by competent persons |
|  | Is the person nominated by the owner as the person responsible for the operation and maintenance of the system competent as defined by the regulations? | $1250 | N/A | 11 |  |
| COMMENTS/ACTIONS TO BE TAKEN (This section should only be completed by an authorised officer) |

# Footnotes

As specified in the Legionella Regulations, a reference to the owner of the premises includes a reference to an occupier of the premises if the occupier is responsible for the operation of the system.

This is the person nominated by the owner as being responsible for the operation and maintenance of the system.

The procedures employed must be adequate to decontaminate all heated sections of the system where temperatures are regularly in the range of ≥25°C to <60°C.